## Front Sheet
Magentically Sensitive Components | Changes | date
Issue 1.6 | HV Rack owner changed to PH | 2012-08-15
Last Updated: 23/10/2012 | changes column added | 2012-08-15
Owners: L. Fry & M.O.M. | PH Moving Beam Stop owner changed to PH | 2012-08-20
Author: L. Fry | Change Tracking added | 2012-08-20
| crane status lights name changed to crane power indication lights | 2012-08-21
NOTE: PLEASE SAVE ANY CHANGES AS AN UPDATED ISSUE & UPLOAD TO MICEmine WEBPAGE | S51,S60,S62 Added to PPS with CMacW as owner. | 2012-10-08
| S61 owner changed to GB | 2012-10-08
| S71,S73 owner changed to HN | 2012-10-08
| Test Centers Sheet Added | 2012-10-23
| Detail to LH2 System added | 2012-11-07
| Risk and Action to remove Risk added for General Power items | 2013-06-07
KEY
Equipment is at Risk & needs further Investigation
Mitigation of Risk - Magnetic Field needs to be evaluated & Confirmed
Risk has been or can be removed
Equipment to be evaluated for Risk
Equipment owner error

## Small Objects (ALL)
Item No. | Object | Location | System | System Owner | Field in air (G) | Magnetic Mass | Risk Level | Comment/Action | Installed
S64 | Thermometer | South East Corner | Infrastructure | Andy Nichols | 0.1 |  |  | Removed, replaced with non-electronic version | YES | System | System Owner
S1 | Fire Break Glass | West Wall | Fire Protection | Ron Lambert/Andy Nichols | 0.5 |  |  |  | YES | AFC | Tom Bradshaw
S2 | Fire Alarm Control Box | West Wall | Fire Protection | Ron Lambert/Andy Nichols | 0.5 |  |  |  | YES | Beam Stop | Geoff Barber
S3 | Fluorescent Exit Sign | West Wall | Infrastructure | Andy Nichols | 0.5 |  |  |  | YES | cKOV | Lucien Cremaldi
S4 | Switch Board D1 | West Wall | General Power | Ian Mullacrane | 0.5 |  | Low | Should be OK at this positiion | YES | Compressed Air | Tim Hayler
S5 | PPS RF Mezz gnd Mag Door Switch | West Wall | PPS | Craig Macwaters | 0.5 |  | Low | Should be OK at this positiion | YES | Conventional Magnets | Henry Nebrensky
S6 | PPS Status Light Circuit Breaker | West Wall | PPS | Craig Macwaters | 0.5 |  |  |  | YES | Decay Solenoid | Vicky Bayliss/Mike Courthold
S7 | Fire Bell and Beacon | West Wall | Fire Protection | Ron Lambert/Andy Nichols | 0.5 |  |  |  | YES | Diffuser | Victoria Blackmore
S8 | Klaxon | West Wall | PPS | Craig Macwaters | 0.5 |  | Low | Should be OK at this positiion | YES | EMR | Ruslan Asfandiarov
S9 | Web Cam | West Wall | Webcams | Henry Nebrensky | 0.5 |  | None | Remove for Installation of West Mezzanine. Decision on whether to reinstate. | YES | Fire Protection | Ron Lambert/Andy Nichols
S26 | Power Isolation Box | North Wall Mezz | General Power | Ian Mullacrane | 0.6 |  | None | Obsolete | YES | General Power | Ian Mullacrane
S12 | Fluorescent Light | North Wall | Infrastructure | Andy Nichols | 0.7 |  |  |  | YES | Global Vacuum | Vishal Francis
S23 | PPS RF Mezz Magnetic Door Switch | North Wall Mezz | PPS | Craig Macwaters | 0.7 |  |  |  | YES | KL | Ludovico Tortora
S27 | Emergency Lighting Contactor | North Wall Mezz | General Power | Ian Mullacrane | 0.7 |  | None | Obsolete | YES | LH2 | Stephen Watson
S13 | PPS Blue/White Light Test Box | North Wall | PPS | Craig Macwaters | 0.8 |  |  |  | YES | Luminosity Monitor | Paul Soler
S24 | PPS RF Mezz Search Junction Box | North Wall Mezz | PPS | Craig Macwaters | 0.8 |  | At Risk | Relay/Pushbuttons fitted maybe affected by magnetic field | YES | MLCR | Craig Macwaters
S11 | D16 Distribution Boards (x4) | North Wall | General Power | Ian Mullacrane | 1 |  | Low | Should be OK at this positiion | YES | Networking | Craig Macwaters
S67 | Pressure Gauge Dial | Trench | Misc | Misc | 1 |  |  |  | YES | PPS | Craig Macwaters
S68 | Control Box for Target | Trench | Target | Paul Smith | 1 |  |  | Disconnected | YES | Radiation Shutter | Norbert Collomb
S20 | Fire Bell and Beacon RF Cage | North Wall | Fire Protection | Ron Lambert/Andy Nichols | 1.3 |  |  |  | YES | RF Distribution | Alan Grant
S28 | Roof Fan Controls | North Wall Mezz | Infrastructure | Andy Nichols | 1.4 |  |  |  | YES | RFCC | Alan DeMello
S69 | Beam Position Box | Trench | ISIS | Martin Hughes | 1.5 |  |  |  | YES | Spectrometer Solenoid | Roy Preece
S70 | Web Cam | Trench | Webcams | Henry Nebrensky | 1.5 |  | At Risk |  | YES | Target | Paul Smith
S71 | Hall Sensor Breakout Box | Trench | Brunel | Henry Nebrensky | 1.5 |  |  |  | YES | TOF0 | Maurizio Bonesini
S72 | Brunel Uni HEP GRP Dial | Trench | Brunel | Henry Nebrensky | 1.5 |  |  |  | YES | TOF1 | Maurizio Bonesini
S73 | DC1 & 2 Polarity Box | Trench | Brunel | Henry Nebrensky | 1.5 |  |  |  | YES | TOF2 | Maurizio Bonesini
S29 | Fire Bell and Beacon N Mezz | North Wall Mezz | Fire Protection | Ron Lambert/Andy Nichols | 1.7 |  |  |  | YES | Tracker | Craig Macwaters
S34 | PPS LH2 Search Junction Box | South Wall Mezz | PPS | Craig Macwaters | 2 |  |  |  | YES | Water | Tim Hayler
S35 | PPS LH2 Magentic Door Switch | South Wall Mezz | PPS | Craig Macwaters | 2 |  |  |  | YES | ISIS | Martin Hughes
S36 | Fire Bell | South Wall Mezz | Fire Protection | Ron Lambert/Andy Nichols | 2 |  |  |  | YES | MISC | Misc
S52 | Linde Gas Analyser | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold | 2 |  |  |  | YES | Infrastructure | Andy Nichols
S74 | mBar Dial | Trench | Misc | Misc | 2 |  |  |  | YES | Webcams | Henry Nebrensky
S81 | Pressure Gauge Dial | Trench | Misc | Misc | 2 |  |  |  | YES | Brunel | Henry Nebrensky
S83 | Flow Meter | Trench | Water | Tim Hayler | 2 |  |  | No risk? | YES | Controls | Pierrick Hanlet
S88 | SouthWest Corner (At height) Distribution Boards | South West Corner | General Power | Ian Mullacrane | 2 |  | Low | Should be OK at this positiion. Otherwise fit Redspot Fuse Board. | YES
S89 | Dist. Board Mounted on Steel Wall | South West Corner | General Power | Ian Mullacrane | 2 |  | At Risk | Change for Redspot Fuse board | YES
S43 | Fire Bell behind SSW | South Wall Ground | Fire Protection | Ron Lambert/Andy Nichols | 3 |  |  |  | YES
S44 | Neutron Monitor 20 DSA wall | South Wall Ground | ISIS | Martin Hughes | 3 |  |  |  | YES
S51 | DSA Indication Box | South East Corner | PPS | Craig Macwaters | 3 |  |  |  | YES
S53 | Fan | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold | 3 |  |  |  | YES
S54 | Flow Meter Panel | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold | 3 |  |  |  | YES
S56 | Air Compressor | South East Corner | Compressed Air | Tim Hayler | 3 |  |  | Disconnected | YES
S58 | DSA Signage Sounder Search Point | South East Corner | PPS | Craig Macwaters | 3 |  |  |  | YES
S60 | DSA ISIS Computer | South East Corner | PPS | Craig Macwaters | 3 |  |  |  | YES
S62 | DSA Muon Beam DSA Light | South East Corner | PPS | Craig Macwaters | 3 |  |  |  | YES
S18 | D4 PSU Distribution Box | North Wall | General Power | Ian Mullacrane | 3.2 |  | None | Redspot fuses fitted and not affected by magnetic field | YES
S45 | Fire Bell | South Wall Ground | Fire Protection | Ron Lambert/Andy Nichols | 4 |  |  |  | YES
S46 | Router | South Wall Ground | Networking | Craig Macwaters | 4 |  |  |  | YES
S47 | Environmental Sensor | South Wall Ground | Controls | Pierrick Hanlet | 4 |  |  |  | YES
S48 | PPS Coil Feed Blue/White Light | South Wall Ground | PPS | Craig Macwaters | 4 |  |  |  | YES
S75 | KLIXON Junction Box 1 & 2 | Trench | General Power | Ian Mullacrane | 4 |  | Not Sure | Not DL Equipment | YES
S76 | D2, Q4-6 Flow Meters | Trench | Water | Tim Hayler | 4 |  |  |  | YES
S77 | Flow Meter Panel 2 & 3 | Trench | Water | Tim Hayler | 4 |  | At Risk | Float Type Switches maybe affected by Magnetic field | YES
S78 | Environmental Sensor | Trench | Controls | Pierrick Hanlet | 4 |  |  |  | YES
S79 | Q7-9 Flow Meters | Trench | Water | Tim Hayler | 4 |  |  |  | YES
S93 | Fluorescent tubes behind SSW | South Wall Ground | Infrastructure | Andy Nichols | 4 |  |  |  | Yes
S31 | Webcam | North Wall Mezz | Webcams | Henry Nebrensky | 4.3 |  |  |  | YES
S16 | PPS RF Cage Magnetic Door Switch (x2) | North Wall | PPS | Craig Macwaters | 4.8 |  |  |  | YES
S30 | Environmental Sensor | North Wall Mezz | Controls | Pierrick Hanlet | 5 |  |  |  | YES
S50 | DSA MCB D11 | South East Corner | General Power | Ian Mullacrane | 5 |  | Low | Should be OK at this positiion | YES
S55 | D5 Distribution Board | South East Corner | General Power | Ian Mullacrane | 5 |  | Low | Should be OK at this positiion | YES
S59 | Fire Bell and Beacon | South East Corner | Fire Protection | Ron Lambert/Andy Nichols | 5 |  |  |  | YES
S84 | Temperature Sensor Box | Trench | Controls | Pierrick Hanlet | 5 |  |  | I think 2, but wasn't 100% sure of which box being discussed | YES
S19 | RF Services D6 Power Feed | North Wall | General Power | Ian Mullacrane | 5.6 |  | None | Redspot fuses fitted and not affected by magnetic field | YES
S15 | Fire Break Glass | North Wall | Fire Protection | Ron Lambert/Andy Nichols | 5.8 |  |  |  | YES
S63 | CMS ION Neutron Monitor | North West Corner | Controls | Pierrick Hanlet | 6 |  |  |  | YES
S14 | Fire Bell and Beacon Lower N wall | North Wall | Fire Protection | Ron Lambert/Andy Nichols | 7.7 |  |  |  | YES
S57 | DSA PPS Magnetic Door Switch | South East Corner | PPS | Craig Macwaters | 8 |  |  |  | YES
S86 | Compressor | Trench | Compressed Air | Tim Hayler | 8 |  |  |  | YES
S92 | PPS Trench Magnetic Switch | Trench | PPS | Craig Macwaters | 9 |  |  | Evaluated without ferrous mass of trench fence work | yes
S65 | Fluorescent Lighting | Throughout | Infrastructure | Andy Nichols | 10 |  |  | Taken at roof height | YES
S85 | Filtration System | Trench | Water | Tim Hayler | 10 |  |  | Just above the air receiver | YES
S88 | Crowcon Gas analyser | North Wall | Infrastructure | Andy Nichols | 10 |  |  |  | YES
S66 | Smoke Detectors | Throughout | Fire Protection | Ron Lambert/Andy Nichols | 10 |  |  | On Ceiling | YES
S87 | D10 Board and Isolator | Trench | General Power | Ian Mullacrane | 15 |  | At Risk | Removal of board. Equipment (Water System) fed from board will be relocated | YES
S49 | Web Cam | South Wall Ground | Webcams | Henry Nebrensky | 20 |  |  |  | YES
S61 | PH Moving Beam Stop |  | Infrastructure | Andy Nichols | 20 |  | At Risk | Motor, Isolator, Control Box & limit switches maybe affected by Magnetic Field | YES
S80 | Fire Bell | Trench | Fire Protection | Ron Lambert/Andy Nichols | 20 |  |  | Dynamic field. 10-20G | YES
S82 | Grundfos Pumps X 2 & control box | Trench | Water | Tim Hayler | 20 |  | At Risk | Dynamic field. Inverters and Control JB may maybe affected by Magnetic field | YES
S33 | Distribution Board D14 | South Wall Mezz | General Power | Ian Mullacrane | 40 |  | At Risk | Change for Redspot Fuse board. Dynamic region | YES
S32 | North Mezz Extension Distribution Board | North Wall Mezz | General Power | Ian Mullacrane | 47 |  | At Risk | Change for Redspot Fuse board | YES
S37 | LH2 Heater PSU | South Wall Mezz | LH2 | Stephen Watson | 200 |  | At Risk | Dynamic field 80-200G | YES
S38 | LH2 Relays | South Wall Mezz | LH2 | Stephen Watson | 200 |  | At Risk | Dynamic field 80-200G | YES
S39 | Pressure Gauge Dial | South Wall Mezz | LH2 | Stephen Watson | 200 |  | At Risk | Dynamic field 80-200G | YES
S40 | D14 LH2 Mezz Power | South Wall Mezz | LH2 | Stephen Watson | 200 |  | At Risk | Dynamic field 80-200G | YES
S10 | D15, D17 & D18(RF) Distribution Boards | North West Corner | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion. Otherwise fit Redspot Fuse Board. | YES
S17 | PPS RF Cage Junction Box | North Wall | PPS | Craig Macwaters |  |  | None | Only Terminals Fitted and not affected by magnetic field | YES
S21 | MCB's | North Wall | General Power | Ian Mullacrane |  |  | At Risk | Dependant on location in the Hall. Solution Fit Redspot fuses | YES
S25 | Old Pressure Gauge Dial | North Wall Mezz | ISIS | Martin Hughes |  |  |  |  | YES | TOF1 | Maurizio Bonesini
S41 | Crane Status Lights | South Wall Mezz | Infrastructure | Andy Nichols |  |  |  |  | YES | TOF1 | Maurizio Bonesini
S42 | PPS Speaker | South Wall Ground | PPS | Craig Macwaters |  |  |  |  | YES
S90 | EMR Control Rack | Cooling Channel | EMR | Ruslan Asfandiarov |  |  |  |  | No
S91 | Diffuser Control Rack | Cooling Channel | Diffuser | Victoria Blackmore |  |  |  |  | No

## Large Objects (ALL)
Item No. | Object | Location | System | System Owner | Field in Air (G) | Magnetic Mass | Risk Level | Notes | Installed | AFC | Tom Bradshaw
L6 | Beam Chopper Rack | North Wall | ISIS | Alan Stevens | 1 |  |  |  | Yes | Beam Stop | Geoff Barber
L14 | Compressor (Sumitomo) (x4) | South Shield Wall | Tracker | Craig Macwaters | 1 |  | Low | Relocated to West Wall. Should be OK at this positiion | Yes | cKOV | Lucien Cremaldi
L7 | Rack | North Wall | Decay Solenoid | Vicky Bayliss/Mike Courthold | 2 |  |  |  | Yes | Compressed Air | Tim Hayler
L8 | Solenoid Rack | North Wall | Decay Solenoid | Vicky Bayliss/Mike Courthold | 2 |  |  |  | Yes | Conventional Magnets | Henry Nebrensky
L13 | HV Rack | South Wall | General Power | Ian Mullacrane | 2.5 |  | Review | Needs additional shielding or Relocating to MLCR (TBA) | Yes | Decay Solenoid | Vicky Bayliss/Mike Courthold
L1 | Sub Station 25 | North Wall | General Power | Ian Mullacrane | 3 |  | Modelling Req'd | Extra Shielding (Extend North Shield Wall) | Yes | Diffuser | Victoria Blackmore
L10 | Air Con Units West | North Wall | Air Conditioning | John Govans | 3 |  |  | without ferrous mass modelled | Yes | EMR | Ruslan Asfandiarov
L17 | Air Con | South Mezz | Air Conditioning | John Govans | 3 |  |  | without ferrous mass modelled | Yes | Fire Protection | Ron Lambert/Andy Nichols
L3 | MQ6-8 | North Wall |  | Mike Courthold | 7 |  |  |  | Yes | General Power | Ian Mullacrane
L16 | Tracker Racks | North Shield Wall | Tracker | Craig Macwaters | 8 |  | Review | Relocate to behind North Shield Wall. Confirm magnetic field level OK | Yes | Global Vacuum | Vishal Francis
L15 | Linde Helium Fridge | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold | 10 |  |  |  | Yes | KL | Ludovico Tortora
L34 | 208v Transformer | Trench | General Power | Ian Mullacrane | 15 |  | At Risk | Relocation 208V Transformer from Trench to RR2 | Yes | LH2 | Stephen Watson
L11 | Cranes | Global |  | Stewart Greenall | 16 |  |  | air field. Will they be operated while magnets on? | Yes | Luminosity Monitor | Paul Soler
L9 | Air Con Units East | North Wall | Air Conditioning | John Govans | 20 |  | At risk? | Without ferrous mass modelled. Field gradinet 5-20G | Yes | MLCR | Craig Macwaters
L36 | MQ9 PSU RACK | Cooling Channel | General Power | Ian Mullacrane | 27 |  | At Risk | Proposed Relocation next to MQ8 PSU Rack | Yes | Networking | Craig Macwaters
L18 | LH2 Gas Panel | South Mezz | LH2 | Stephen Watson | 80 to 200 |  |  |  | Yes | PPS | Craig Macwaters
L19 | Spectrometer Solenoid | Cooling Channel | Spectrometer Solenoid | Roy Preece |  |  |  |  | No | RF Distribution | Alan Grant
L2 | Linac Shield Wall | North Wall |  |  |  |  | None | not sensitive itself but has it been included in models as a magnetic mass? | Yes | RFCC | Alan DeMello
L20 | AFC | Cooling Channel | AFC | Tom Bradshaw |  |  |  |  | No | Spectrometer Solenoid | Roy Preece
L21 | Spectrometer Solenoid 2 | Cooling Channel | Spectrometer Solenoid | Roy Preece |  |  |  |  | No | Target | Paul Smith
L22 | KL | Cooling Channel | KL | Ludovico Tortora |  |  |  |  | No | TOF0 | Maurizio Bonesini
L23 | EMR | Cooling Channel | EMR | Ruslan Asfandiarov |  |  |  |  | No | TOF1 | Maurizio Bonesini
L24 | TOF2 | Cooling Channel | TOF2 | Maurizio Bonesini |  |  |  |  | No | TOF2 | Maurizio Bonesini
L25 | RF System | Cooling Channel | RF Distribution | Alan Grant |  |  | Review at Step 5/6 | Relevant at Steps 5 & 6 Only | No | Tracker | Craig Macwaters
L26 | RF Tiara | Cooling Channel/North Wall | RF Distribution | Alan Grant |  |  | low | This is only relevant for Step 4 and will not be in use when Step 4 equipment is running | No | Water | Tim Hayler
L27 | RF Cooling water Panels | North Shield Wall | RF Distribution | Alan Grant |  |  | At Risk | Equipment in Water Panels will be chosen so as not to be susceptible to Magnetic Fields | No
L28 | Global Vacuum System | Global | Global Vacuum | Vishal Francis |  |  |  | Relocated to top of South Mezz | No
L29 | RFCC Control Rack X7 | North Wall | RFCC | Alan DeMello |  |  |  |  | No
L30 | RFCC Control Rack X2 | Upstream CC | RFCC | Alan DeMello |  |  |  |  | No
L31 | Tracker Cryocooler | SS1 | Tracker | Craig Macwaters |  |  | Under Review | Weiner PSU (250)/ Turbo Molecular Pump (5) | No
L32 | Tracker Cryocooler | SS2 | Tracker | Craig Macwaters |  |  | Under Review | Weiner PSU (250)/ Turbo Molecular Pump (5) | No
L33 | Compressor (cryomech) (x3) | South Shield Wall | LH2 | Stephen Watson |  |  | At Risk | Relocated to West Wall. Should be OK at this position | Yes
L35 | Vac/Compressor Control Rack | North West Corner | General Power | Ian Mullacrane |  |  | Low | Should be OK at this position | Yes
L4 | MD1 | North Wall |  | Mike Courthold |  |  |  |  | Yes
L5 | MQ1-3 | North Wall |  | Mike Courthold |  |  |  |  | Yes

## Fire Protection (AN)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S1 | Fire Break Glass | West Wall | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S2 | Fire Alarm Control Box | West Wall | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S7 | Fire Bell and Beacon | West Wall | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S14 | Fire Bell and Beacon | North Wall | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S15 | Fire Break Glass | North Wall | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S20 | Fire Bell and Beacon | North Wall | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S29 | Fire Beacon | North Wall Mezz | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S36 | Fire Bell | South Wall Mezz | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S43 | Fire Bell and Beacon | South Wall Ground | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S45 | Fire Bell | South Wall Ground | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S59 | Fire Bell and Beacon | South East Corner | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S66 | Smoke Detectors | Throughout | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes
S80 | Fire Bell | Trench | Fire Protection | Ron Lambert/Andy Nichols |  |  |  |  | Yes

## General Power (IM)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S4 | Switch Board D1 | West Wall | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion | Yes
S10 | D15, D17 & D18(RF) Distribution Boards | North West Corner | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion | Yes
S11 | D16 Distribution Boards (x4) | North Wall | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion | Yes
S18 | D4 PSU Distribution Box | North Wall | General Power | Ian Mullacrane |  |  | None | Redspot fuses fitted and not affected by magnetic field | Yes
S19 | RF Services D6 Power Feed | North Wall | General Power | Ian Mullacrane |  |  | None | Redspot fuses fitted and not affected by magnetic field | Yes
S21 | MCB's | North Wall | General Power | Ian Mullacrane |  |  | At Risk | Dependant on location in the Hall. Solution Fit Redspot fuses | Yes
S26 | Power Isolation Box | North Wall Mezz | General Power | Ian Mullacrane |  |  | Remove | Obsolete | Yes
S27 | Emergency Lighting Contactor | North Wall Mezz | General Power | Ian Mullacrane |  |  | Remove | Obsolete | Yes
S32 | North Mezz Extension Distribution Board | North Wall Mezz | General Power | Ian Mullacrane |  |  | At Risk | Change for Redspot Fuse board | Yes
S33 | Distribution Board | South Wall Mezz | General Power | Ian Mullacrane |  |  | At Risk | Change for Redspot Fuse board | Yes
S50 | DSA MCB D11 | South East Corner | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion | Yes
S55 | D5 Distribution Board | South East Corner | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion | Yes
S75 | KLIXON Junction Box 1 & 2 | Trench | General Power | Ian Mullacrane |  |  | Not sure | Not DL kit | Yes
S87 | D10 Board and Isolator | Trench | General Power | Ian Mullacrane |  |  | At Risk | Removal of board. Equipment fed from board planned to be relocated | Yes
S88 | SouthWest Corner (At height) Distribution Boards | South West Corner | General Power | Ian Mullacrane |  |  | Low | Should be OK at this positiion. Otherwise fit Redspot Fuse Board. | YES
L1 | Sub Station 25 | North Wall | General Power | Ian Mullacrane |  |  | Modelling Req'd | Extra Shielding (Extend North Shield Wall) | Yes
L13 | HV Rack | South Wall | General Power | Ian Mullacrane |  |  | At Risk | Needs additional shielding or Relocating to MLCR (TBA) | Yes
L33 | 208v Transformer | Trench | General Power | Ian Mullacrane |  |  | At Risk | Relocation of 208v Transformer from Trench to RR2 | Yes

## PPS (CM)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S5 | PPS Magnetic Door Switch | West Wall | PPS | Craig Macwaters |  |  | low | Should be OK at this positiion | Yes
S6 | PPS Status Light Circuit Breaker | West Wall | PPS | Craig Macwaters |  |  |  |  | Yes
S8 | Klaxon | West Wall | PPS | Craig Macwaters |  |  | low | Should be OK at this positiion | Yes
S13 | PPS Blue/White Light Test Box | North Wall | PPS | Craig Macwaters |  |  |  |  | Yes
S16 | RF Cage PPS Magnetic Door Switch (x2) | North Wall | PPS | Craig Macwaters |  |  |  |  | Yes
S17 | RF Cage PPS Junction Box | North Wall | PPS | Craig Macwaters |  |  | None | Only Terminals Fitted and not affected by magnetic field | Yes
S22 | Magnet ON Light PPS | North Wall | PPS | Craig Macwaters |  |  |  |  | Yes
S23 | PPS Magnetic Door Switch | North Wall Mezz | PPS | Craig Macwaters |  |  |  |  | Yes
S34 | PPS LH2 Search Junction Box | South Wall Mezz | PPS | Craig Macwaters |  |  |  |  | Yes
S35 | PPS LH2 Magentic Door Switch | South Wall Mezz | PPS | Craig Macwaters |  |  |  |  | Yes
S42 | PPS Speaker | South Wall Ground | PPS | Craig Macwaters |  |  |  |  | Yes
S48 | PPS Coil Feed Blue/White Light | South Wall Ground | PPS | Craig Macwaters |  |  |  |  | Yes
S57 | DSA PPS Magnetic Door Switch | South East Corner | PPS | Craig Macwaters |  |  |  |  | Yes
S58 | DSA Signage Sounder Search Point | South East Corner | PPS | Craig Macwaters |  |  |  |  | Yes

## LH2 (SW)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S37 | LH2 Heater PSU | South Wall Mezz | LH2 | Stephen Watson |  |  |  |  | Yes
S38 | LH2 Relays | South Wall Mezz | LH2 | Stephen Watson |  |  |  |  | Yes
S39 | Pressure Gauge Dial | South Wall Mezz | LH2 | Stephen Watson |  |  |  |  | Yes
S40 | D14 LH2 Mezz Power | South Wall Mezz | LH2 | Stephen Watson |  |  |  |  | Yes
L18 | LH2 Gas Panel | South Mezz | LH2 | Stephen Watson | Regulator Valves, Hydride Bed [metal Hydride Material] |  |  |  | Yes

## RF Distribution (AG)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S24 | RF Mezz Search Junction Box | North Wall Mezz | RF Distribution | Alan Grant |  |  | At Risk | Relay/Pushbuttons Fitted maybe affected by magnetic field | Yes

## Decay Solenoid (MC)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S51 | DSA Indication Box | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | Yes
S60 | DSA ISIS Computer | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | Yes
S62 | DSA Muon Beam DSA Light | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | Yes
L8 | Solenoid Rack | North Wall | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | Yes
L15 | Linde Helium Fridge | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | Yes
L7 | Rack-Gas Pipes etc | North Wall | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | Yes
S52 | Linde Gas Analyser | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | YES
S53 | Fan | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | YES
S54 | Flow Meter Panel | South East Corner | Decay Solenoid | Vicky Bayliss/Mike Courthold |  |  |  |  | YES

## Infrastructure (SG)
Item No. | Object | Location | System | System Owner | Sensitive Components (Max in Air [Gauss]) | Magnetic Mass | Risk Level | Notes | Installed
S3 | Fluorescent Exit Sign | West Wall | Infrastructure | Stewart Greenall |  |  |  |  | YES
S12 | Fluorescent Light | North Wall | Infrastructure | Stewart Greenall |  |  |  |  | YES
S28 | Roof Fan Controls | North Wall Mezz | Infrastructure | Stewart Greenall |  |  |  |  | YES
S41 | Crane Status Lights | South Wall Mezz | Infrastructure | Stewart Greenall |  |  |  |  | YES
S61 | PH Moving Beam Stop |  | Infrastructure | Stewart Greenall |  |  |  |  | YES
S65 | Fluorescent Lighting | Throughout | Infrastructure | Stewart Greenall |  |  |  |  | YES

## Magnetic Masses
Magnetic Masses to be Considered in Magnetic Model
Linac Shield Wall
Buried Magnets Behind Beam Dump
False Floor Structure
DSA Block House
North Mezz
South Mezz Stairs
Transformer Wall
PPS Cages
Trench Flooring
False Floor Behind North Shield Wall

## Test Centers
Test Centers for Magnetic Compatibility Tests
Facility | Location | Type | Max Size | Max Guass | Contact | Confirmed for Use
Karlsruhe Institute of Technology | Karlsruhe, Germany | Helmholtz | 1m | 200G | Vishal Francis | YES
INFN | Frascati, Italy | Helmholtz | 900mm | 60G | Maurizio Bonesini | YES
University of Oxford | Oxford, UK | Helmholtz |  |  | John Cobb
Rutherford Appleton Laboratory | Chilton, UK | Magnet under test | n/a |  | Andy Nichols | YES
Daresbury Laboratory | Warringotn, UK | Helmholtz
LBNL | Berkely, USA | Magnet under test | n/a |  | Roy Preece | YES
FOR DISCUSSION ONLY